## Registers
Unipi 1.1
Holding registers | [6 empty] | v1.0
Register Address |  | Length | R/W | Data Type | Content | Bit Nr. | Category
DEC | HEX
0 | 0x0000 | 1 | R | MixedBits | Digital Inputs |  | Basic
[5 empty] | Digital Input 1 | 0
[5 empty] | Digital Input 2 | 1
[5 empty] | Digital Input 3 | 2
[5 empty] | Digital Input 4 | 3
[5 empty] | Digital Input 5 | 4
[5 empty] | Digital Input 6 | 5
[5 empty] | Digital Input 7 | 6
[5 empty] | Digital Input 8 | 7
[5 empty] | Digital Input 9 | 8
[5 empty] | Digital Input 10 | 9
[5 empty] | Digital Input 11 | 10
[5 empty] | Digital Input 12 | 11
1 | 0x0001 | 1 | RW | MixedBits | Relay outputs |  | Basic
[5 empty] | Relay output 1 | 0
[5 empty] | Relay output 2 | 1
[5 empty] | Relay output 3 | 2
[5 empty] | Relay output 4 | 3
[5 empty] | Relay output 5 | 4
[5 empty] | Relay output 6 | 5
[5 empty] | Relay output 7 | 6
[5 empty] | Relay output 8 | 7
2 | 0x0002 | 1 | RW | int16 / int | Analog Output value 1 (0..4000 ~ 0..10V) |  | Basic
3 | 0x0003 | 2 | R | float / real | Analog Input value 1 |  | Basic
5 | 0x0005 | 2 | R | float / real | Analog Input value 2 |  | Basic
7 | 0x0007 | 2 | RW | uint32 / udint | Counter of Digital Input 1 |  | Basic
9 | 0x0009 | 2 | RW | uint32 / udint | Counter of Digital Input 2 |  | Basic
11 | 0x000B | 2 | RW | uint32 / udint | Counter of Digital Input 3 |  | Basic
13 | 0x000D | 2 | RW | uint32 / udint | Counter of Digital Input 4 |  | Basic
15 | 0x000F | 2 | RW | uint32 / udint | Counter of Digital Input 5 |  | Basic
17 | 0x0011 | 2 | RW | uint32 / udint | Counter of Digital Input 6 |  | Basic
19 | 0x0013 | 2 | RW | uint32 / udint | Counter of Digital Input 7 |  | Basic
21 | 0x0015 | 2 | RW | uint32 / udint | Counter of Digital Input 8 |  | Basic
23 | 0x0017 | 2 | RW | uint32 / udint | Counter of Digital Input 9 |  | Basic
25 | 0x0019 | 2 | RW | uint32 / udint | Counter of Digital Input 10 |  | Basic
27 | 0x001B | 2 | RW | uint32 / udint | Counter of Digital Input 11 |  | Basic
29 | 0x001D | 2 | RW | uint16 / uint | Counter of Digital Input 12 |  | Basic
1010 | 0x03F2 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 1 |  | Advanced
1011 | 0x03F3 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 2 |  | Advanced
1012 | 0x03F4 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 3 |  | Advanced
1013 | 0x03F5 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 4 |  | Advanced
1014 | 0x03F6 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 5 |  | Advanced
1015 | 0x03F7 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 6 |  | Advanced
1016 | 0x03F8 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 7 |  | Advanced
1017 | 0x03F9 | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 8 |  | Advanced
1018 | 0x03FA | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 9 |  | Advanced
1019 | 0x03FB | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 10 |  | Advanced
1020 | 0x03FC | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 11 |  | Advanced
1021 | 0x03FD | 1 | RW | uint16 / uint | Debounce time (in 100μs) for DI 12 |  | Advanced
1022 | 0x03FE | 1 | RW | uint16 / uint | Analog Output PWM frequency |  | Expert
1023 | 0x03FF | 1 | RW | uint16 / uint | Analog Input 1 resolution |  | Expert
1024 | 0x0400 | 1 | RW | uint16 / uint | Analog Input 2 resolution |  | Expert

## Coils
Unipi 1.1
Coils |  |  |  | v1.0
Register Address |  | R/W | Content | Category
DEC | HEX
0 | 0x0000 | RW | Relay output 1 | Basic
1 | 0x0001 | RW | Relay output 2 | Basic
2 | 0x0002 | RW | Relay output 3 | Basic
3 | 0x0003 | RW | Relay output 4 | Basic
4 | 0x0004 | RW | Relay output 5 | Basic
5 | 0x0005 | RW | Relay output 6 | Basic
6 | 0x0006 | RW | Relay output 7 | Basic
7 | 0x0007 | RW | Relay output 8 | Basic

## Description
Unipi 1.1
Description |  |  |  |  | v1.0
Check out the Unipi Knowledge base for more information
Byte order
0-LSB, 15-MSB
Default configuration/values
|  | Data | Value | Description
| DI | Counter | 0 | -
|  | Debounce | 0 | 0 ms
| AI | State | 0 | OFF
|  | Resolution | 18 | bits of resolution
| RO | State | 0 | OFF
Note: configuration is not permanently saved, set on each power-on